{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Tabelle1"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Tabelle1","index":0,"n_rows":9,"n_cols":14,"rows_kept":9,"cut":false,"hidden":false,"merged":[]}
[null,null,null,"Rohrleitung",null,null,null,null,null,"Armatur"]
["Dichte ρ",997,"kg/m3",null,"di [mm]","l [mm]","λ","v [m/s]","ΔpR [Pa]",null,"Bezeichnung","ζ","v [m/s]","ΔpA [Pa]"]
["dyn. Viskosität η",1.1999999999999999E-3,"kg/(m s)",null,82.5,10000,3.1E-2,0.3,{"$f":"G3*F3/E3*Dichte*H3^2","v":337.16727272727275},null,"U-Bogen",0.32,0.3,{"$f":"R9","v":0}]
["kin. Viskosität υ",{"$f":"DynVisk/Dichte","v":1.2036108324974924E-6},"m2/s",null,37.200000000000003,6000,3.1E-2,{"$f":"E$3^2/E4^2/2*H$3","v":0.73775689386056176},{"$f":"G4*F4/E4*Dichte*H4^2","v":2713.2618936773392},null,"90-Krümmer",0.21,0.3,{"$f":"L4*Dichte*M4^2","v":18.843299999999999}]
[null,null,null,null,37.200000000000003,12000,3.1E-2,{"$f":"E$3^2/E5^2/2*H$3","v":0.73775689386056176},{"$f":"G5*F5/E5*Dichte*H5^2","v":5426.5237873546785},null,"Schieber",0.3,0.3,{"$f":"L5*Dichte*M5^2","v":26.918999999999997}]
[null,null,null,null,null,null,null,null,null,null,"Ventil",0.4,0.74,{"$f":"L6*Dichte*M6^2","v":218.38288}]
[null,null,null,null,null,null,null,null,null,null,"Ventil",0.4,0.74,{"$f":"L7*Dichte*M7^2","v":218.38288}]
[null,null,null,null,null,null,null,null,null,null,"Eckventil",0.2,0.74,{"$f":"L8*Dichte*M8^2","v":109.19144}]
["Druckverlust",{"$f":"SUM(I3:I5,N3:N9)/1000","v":9.1778638937592891},"kPa",null,null,null,null,null,null,null,"Eckventil",0.2,0.74,{"$f":"L9*Dichte*M9^2","v":109.19144}]